Product Substitution Request

SR-081 · Mission Bay Data Center · P-401 Chilled Water Pump

BuildCrew recommends replacing the delayed specified pump with the Armstrong 4030 4×3×10. The proposed unit satisfies all 31 hard requirements, arrives before the required-on-site date, and passes project BIM coordination with one minor 25 mm piping adjustment.

# Decision requested

Approve this package for submission to the mechanical engineer. This internal approval authorizes engineering review and a temporary inventory hold only; it does not authorize a purchase order or a permanent project-model update.

| Technical | Coordination | Delivery | Commercial |
| --- | --- | --- | --- |
| 31 / 31 requirements | 0 critical clashes | Aug 19 · 9 days early | $31,680 installed |

# Reason for substitution

The specified pump is delayed by 77 days because of a manufacturer component shortage. The revised ship date falls after chilled-water commissioning and exposes the project critical path.

# Technical equivalence

| Requirement | Specified | Proposed | Evidence | Result |
| --- | --- | --- | --- | --- |
| Design flow | 420 gpm | 420 gpm | M-601 / P-401 | Pass |
| Design head | 96 ft | 98 ft | Data sheet / p. 4 | Pass |
| Inlet connection | 4 in FLG | 4 in FLG | Submittal / sheet 6 | Pass |
| Outlet connection | 3 in FLG | 3 in FLG | Submittal / sheet 6 | Pass |
| Motor | 15 HP · 480 V | 15 HP · 480 V | Data sheet / p. 5 | Pass |
| Overall envelope | ≤ 1,900 mm | 1,780 mm | Dimension sheet / 6 | Pass |
| Certification | UL listed | UL listed | UL certificate | Pass |

# BIM coordination findings

BuildCrew generated an IFC4 and GLB object from verified manufacturer dimensions, placed it at P-401, and checked equipment envelope, connectors, maintenance clearance, and adjacent systems.

| Check | Finding | Required action |
| --- | --- | --- |
| Hard clash | None | No structural change |
| Motor clearance | 915 mm preserved | No action |
| Suction connection | 25 mm offset | Provide 25 mm spool adjustment |
| Installation access | Pass | No action |

# Cost and schedule effect

Total installed cost is $31,680, a $4,260 increase over the delayed specified unit. The recommended replacement is available for delivery on August 19, preserving the August 28 required-on-site milestone and avoiding a modeled 77-day procurement delay.

# Evidence and files

Replacement BIM: candidate-c.ifc and candidate-c.glb

Coordination issues: candidate-c-coordination.bcfzip

Source map and confidence report: source-map.json and confidence-report.json

Commercial comparison: BuildCrew_Quote_Leveling.xlsx

Manufacturer drawing set: P-401_Manufacturer_Drawings.pdf